## Devices
rack | u | model | name | role | height_u | power_cords | serial | owner | warranty_end | runs
R001 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r001 |  |  | AB |  | AI tenant (imagined)
R002 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r002 |  |  | AB |  | AI tenant (imagined)
R003 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r003 |  |  | AB |  | AI tenant (imagined)
R004 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r004 |  |  | AB |  | AI tenant (imagined)
R005 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r005 |  |  | AB |  | AI tenant (imagined)
R006 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r006 |  |  | AB |  | AI tenant (imagined)
R007 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r007 |  |  | AB |  | AI tenant (imagined)
R008 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r008 |  |  | AB |  | AI tenant (imagined)
R009 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r009 |  |  | AB |  | AI tenant (imagined)
R010 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r010 |  |  | AB |  | AI tenant (imagined)
R011 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r011 |  |  | AB |  | AI tenant (imagined)
R012 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r012 |  |  | AB |  | AI tenant (imagined)
R013 | 40 | switch/arista/7060x5-64d | leaf-a |  |  | AB
R014 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r014 |  |  | AB |  | AI tenant (imagined)
R015 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r015 |  |  | AB |  | AI tenant (imagined)
R016 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r016 |  |  | AB |  | AI tenant (imagined)
R017 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r017 |  |  | AB |  | AI tenant (imagined)
R018 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r018 |  |  | AB |  | AI tenant (imagined)
R019 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r019 |  |  | AB |  | AI tenant (imagined)
R020 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r020 |  |  | AB |  | AI tenant (imagined)
R021 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r021 |  |  | AB |  | AI tenant (imagined)
R022 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r022 |  |  | AB |  | AI tenant (imagined)
R023 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r023 |  |  | AB |  | AI tenant (imagined)
R024 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r024 |  |  | AB |  | AI tenant (imagined)
R025 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r025 |  |  | AB |  | AI tenant (imagined)
R026 | 40 | switch/arista/7060x5-64d | leaf-b |  |  | AB
R027 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r027 |  |  | AB |  | AI tenant (imagined)
R028 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r028 |  |  | AB |  | AI tenant (imagined)
R029 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r029 |  |  | AB |  | AI tenant (imagined)
R030 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r030 |  |  | AB |  | AI tenant (imagined)
R031 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r031 |  |  | AB |  | AI tenant (imagined)
R032 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r032 |  |  | AB |  | AI tenant (imagined)
R033 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r033 |  |  | AB |  | AI tenant (imagined)
R034 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r034 |  |  | AB |  | AI tenant (imagined)
R035 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r035 |  |  | AB |  | AI tenant (imagined)
R036 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r036 |  |  | AB |  | AI tenant (imagined)
R037 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r037 |  |  | AB |  | AI tenant (imagined)
R038 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r038 |  |  | AB |  | AI tenant (imagined)
R039 | 40 | switch/arista/7060x5-64d | leaf-c |  |  | AB
R040 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r040 |  |  | AB |  | AI tenant (imagined)
R041 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r041 |  |  | AB |  | AI tenant (imagined)
R042 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r042 |  |  | AB |  | AI tenant (imagined)
R043 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r043 |  |  | AB |  | AI tenant (imagined)
R044 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r044 |  |  | AB |  | AI tenant (imagined)
R045 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r045 |  |  | AB |  | AI tenant (imagined)
R046 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r046 |  |  | AB |  | AI tenant (imagined)
R047 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r047 |  |  | AB |  | AI tenant (imagined)
R048 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r048 |  |  | AB |  | AI tenant (imagined)
R049 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r049 |  |  | AB |  | AI tenant (imagined)
R050 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r050 |  |  | AB |  | AI tenant (imagined)
R051 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r051 |  |  | AB |  | AI tenant (imagined)
R052 | 40 | switch/arista/7060x5-64d | leaf-d |  |  | AB
R053 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r053 |  |  | AB |  | AI tenant (imagined)
R054 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r054 |  |  | AB |  | AI tenant (imagined)
R055 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r055 |  |  | AB |  | AI tenant (imagined)
R056 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r056 |  |  | AB |  | AI tenant (imagined)
R057 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r057 |  |  | AB |  | AI tenant (imagined)
R058 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r058 |  |  | AB |  | AI tenant (imagined)
R059 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r059 |  |  | AB |  | AI tenant (imagined)
R060 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r060 |  |  | AB |  | AI tenant (imagined)
R061 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r061 |  |  | AB |  | AI tenant (imagined)
R062 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r062 |  |  | AB |  | AI tenant (imagined)
R063 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r063 |  |  | AB |  | AI tenant (imagined)
R064 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r064 |  |  | AB |  | AI tenant (imagined)
R065 | 40 | switch/arista/7060x5-64d | leaf-e |  |  | AB
R066 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r066 |  |  | AB |  | AI tenant (imagined)
R067 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r067 |  |  | AB |  | AI tenant (imagined)
R068 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r068 |  |  | AB |  | AI tenant (imagined)
R069 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r069 |  |  | AB |  | AI tenant (imagined)
R070 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r070 |  |  | AB |  | AI tenant (imagined)
R071 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r071 |  |  | AB |  | AI tenant (imagined)
R072 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r072 |  |  | AB |  | AI tenant (imagined)
R073 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r073 |  |  | AB |  | AI tenant (imagined)
R074 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r074 |  |  | AB |  | AI tenant (imagined)
R075 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r075 |  |  | AB |  | AI tenant (imagined)
R076 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r076 |  |  | AB |  | AI tenant (imagined)
R077 | 1 | rack_system/nvidia/gb200-nvl72 | nvl72-r077 |  |  | AB |  | AI tenant (imagined)
R078 | 40 | switch/arista/7060x5-64d | leaf-f |  |  | AB
R079 | 2 | switch/arista/7800r3-chassis | spine-1 |  |  | AB
R079 | 20 | switch/arista/7800r3-chassis | spine-2 |  |  | AB

## Cables
from_device | from_port | to_device | to_port | type | phase | media | speed | length_m | color | label | vlan | route

## Sites
site | city | country | lat | lon | timezone | role | provider | it_kw | pue

## Rooms
room | site | length_m | width_m | height_m | raised_floor_mm | lighting_w | timezone
Pod hall | FJD-1 | 16.2 | 26 | 5 | 0 |  | Europe/Oslo

## Racks
rack | row | room | position | height_u | width_in | front_faces | max_kw
R001 | Row A | Pod hall | 1 | 48 | 19 | A | 138
R002 | Row A | Pod hall | 2 | 48 | 19 | A | 138
R003 | Row A | Pod hall | 3 | 48 | 19 | A | 138
R004 | Row A | Pod hall | 4 | 48 | 19 | A | 138
R005 | Row A | Pod hall | 5 | 48 | 19 | A | 138
R006 | Row A | Pod hall | 6 | 48 | 19 | A | 138
R007 | Row A | Pod hall | 7 | 48 | 19 | A | 138
R008 | Row A | Pod hall | 8 | 48 | 19 | A | 138
R009 | Row A | Pod hall | 9 | 48 | 19 | A | 138
R010 | Row A | Pod hall | 10 | 48 | 19 | A | 138
R011 | Row A | Pod hall | 11 | 48 | 19 | A | 138
R012 | Row A | Pod hall | 12 | 48 | 19 | A | 138
R013 | Row A | Pod hall | 13 | 48 | 19 | A | 15
R014 | Row B | Pod hall | 1 | 48 | 19 | B | 138
R015 | Row B | Pod hall | 2 | 48 | 19 | B | 138
R016 | Row B | Pod hall | 3 | 48 | 19 | B | 138
R017 | Row B | Pod hall | 4 | 48 | 19 | B | 138
R018 | Row B | Pod hall | 5 | 48 | 19 | B | 138
R019 | Row B | Pod hall | 6 | 48 | 19 | B | 138
R020 | Row B | Pod hall | 7 | 48 | 19 | B | 138
R021 | Row B | Pod hall | 8 | 48 | 19 | B | 138
R022 | Row B | Pod hall | 9 | 48 | 19 | B | 138
R023 | Row B | Pod hall | 10 | 48 | 19 | B | 138
R024 | Row B | Pod hall | 11 | 48 | 19 | B | 138
R025 | Row B | Pod hall | 12 | 48 | 19 | B | 138
R026 | Row B | Pod hall | 13 | 48 | 19 | B | 15
R027 | Row C | Pod hall | 1 | 48 | 19 | A | 138
R028 | Row C | Pod hall | 2 | 48 | 19 | A | 138
R029 | Row C | Pod hall | 3 | 48 | 19 | A | 138
R030 | Row C | Pod hall | 4 | 48 | 19 | A | 138
R031 | Row C | Pod hall | 5 | 48 | 19 | A | 138
R032 | Row C | Pod hall | 6 | 48 | 19 | A | 138
R033 | Row C | Pod hall | 7 | 48 | 19 | A | 138
R034 | Row C | Pod hall | 8 | 48 | 19 | A | 138
R035 | Row C | Pod hall | 9 | 48 | 19 | A | 138
R036 | Row C | Pod hall | 10 | 48 | 19 | A | 138
R037 | Row C | Pod hall | 11 | 48 | 19 | A | 138
R038 | Row C | Pod hall | 12 | 48 | 19 | A | 138
R039 | Row C | Pod hall | 13 | 48 | 19 | A | 15
R040 | Row D | Pod hall | 1 | 48 | 19 | B | 138
R041 | Row D | Pod hall | 2 | 48 | 19 | B | 138
R042 | Row D | Pod hall | 3 | 48 | 19 | B | 138
R043 | Row D | Pod hall | 4 | 48 | 19 | B | 138
R044 | Row D | Pod hall | 5 | 48 | 19 | B | 138
R045 | Row D | Pod hall | 6 | 48 | 19 | B | 138
R046 | Row D | Pod hall | 7 | 48 | 19 | B | 138
R047 | Row D | Pod hall | 8 | 48 | 19 | B | 138
R048 | Row D | Pod hall | 9 | 48 | 19 | B | 138
R049 | Row D | Pod hall | 10 | 48 | 19 | B | 138
R050 | Row D | Pod hall | 11 | 48 | 19 | B | 138
R051 | Row D | Pod hall | 12 | 48 | 19 | B | 138
R052 | Row D | Pod hall | 13 | 48 | 19 | B | 15
R053 | Row E | Pod hall | 1 | 48 | 19 | A | 138
R054 | Row E | Pod hall | 2 | 48 | 19 | A | 138
R055 | Row E | Pod hall | 3 | 48 | 19 | A | 138
R056 | Row E | Pod hall | 4 | 48 | 19 | A | 138
R057 | Row E | Pod hall | 5 | 48 | 19 | A | 138
R058 | Row E | Pod hall | 6 | 48 | 19 | A | 138
R059 | Row E | Pod hall | 7 | 48 | 19 | A | 138
R060 | Row E | Pod hall | 8 | 48 | 19 | A | 138
R061 | Row E | Pod hall | 9 | 48 | 19 | A | 138
R062 | Row E | Pod hall | 10 | 48 | 19 | A | 138
R063 | Row E | Pod hall | 11 | 48 | 19 | A | 138
R064 | Row E | Pod hall | 12 | 48 | 19 | A | 138
R065 | Row E | Pod hall | 13 | 48 | 19 | A | 15
R066 | Row F | Pod hall | 1 | 48 | 19 | B | 138
R067 | Row F | Pod hall | 2 | 48 | 19 | B | 138
R068 | Row F | Pod hall | 3 | 48 | 19 | B | 138
R069 | Row F | Pod hall | 4 | 48 | 19 | B | 138
R070 | Row F | Pod hall | 5 | 48 | 19 | B | 138
R071 | Row F | Pod hall | 6 | 48 | 19 | B | 138
R072 | Row F | Pod hall | 7 | 48 | 19 | B | 138
R073 | Row F | Pod hall | 8 | 48 | 19 | B | 138
R074 | Row F | Pod hall | 9 | 48 | 19 | B | 138
R075 | Row F | Pod hall | 10 | 48 | 19 | B | 138
R076 | Row F | Pod hall | 11 | 48 | 19 | B | 138
R077 | Row F | Pod hall | 12 | 48 | 19 | B | 138
R078 | Row F | Pod hall | 13 | 48 | 19 | B | 15
R079 | Spine | Pod hall | 1 | 48 | 19 | A | 40

## Power
name | type | rating | fed_from | feed | rack | voltage | phases | phase | runtime_min | battery_kwh | model
Substation (400 kV, imagined) | utility | 21600 kW
Genset bank A (6 × Cat 3516C) | generator | 12000 kW | [8 empty] | genset/cat/3516c
ATS A | ATS | 10800 kW | Substation (400 kV, imagined); Genset bank A (6 × Cat 3516C) | A
Transformer A | transformer | 10800 kW | ATS A | A
Switchboard A | switchboard | 10800 kW | Transformer A | A
UPS bank A | UPS | 9504 kW | Switchboard A | A | [5 empty] | 792
Mechanical UPS A | UPS | 1728 kW | Switchboard A | A | [5 empty] | 288
Mechanical board A | switchboard | 1728 kW | Mechanical UPS A | A
Genset bank B (6 × Cat 3516C) | generator | 12000 kW | [8 empty] | genset/cat/3516c
ATS B | ATS | 10800 kW | Substation (400 kV, imagined); Genset bank B (6 × Cat 3516C) | B
Transformer B | transformer | 10800 kW | ATS B | B
Switchboard B | switchboard | 10800 kW | Transformer B | B
UPS bank B | UPS | 9504 kW | Switchboard B | B | [5 empty] | 792
Mechanical UPS B | UPS | 1728 kW | Switchboard B | B | [5 empty] | 288
Mechanical board B | switchboard | 1728 kW | Mechanical UPS B | B
Row A busway A | busway | 1656 kW | UPS bank A | A
Row A busway B | busway | 1656 kW | UPS bank B | B
R001 tap A | busway | 132 kW | Row A busway A | A | R001 | 400 | 3
R001 tap B | busway | 132 kW | Row A busway B | B | R001 | 400 | 3
R002 tap A | busway | 132 kW | Row A busway A | A | R002 | 400 | 3
R002 tap B | busway | 132 kW | Row A busway B | B | R002 | 400 | 3
R003 tap A | busway | 132 kW | Row A busway A | A | R003 | 400 | 3
R003 tap B | busway | 132 kW | Row A busway B | B | R003 | 400 | 3
R004 tap A | busway | 132 kW | Row A busway A | A | R004 | 400 | 3
R004 tap B | busway | 132 kW | Row A busway B | B | R004 | 400 | 3
R005 tap A | busway | 132 kW | Row A busway A | A | R005 | 400 | 3
R005 tap B | busway | 132 kW | Row A busway B | B | R005 | 400 | 3
R006 tap A | busway | 132 kW | Row A busway A | A | R006 | 400 | 3
R006 tap B | busway | 132 kW | Row A busway B | B | R006 | 400 | 3
R007 tap A | busway | 132 kW | Row A busway A | A | R007 | 400 | 3
R007 tap B | busway | 132 kW | Row A busway B | B | R007 | 400 | 3
R008 tap A | busway | 132 kW | Row A busway A | A | R008 | 400 | 3
R008 tap B | busway | 132 kW | Row A busway B | B | R008 | 400 | 3
R009 tap A | busway | 132 kW | Row A busway A | A | R009 | 400 | 3
R009 tap B | busway | 132 kW | Row A busway B | B | R009 | 400 | 3
R010 tap A | busway | 132 kW | Row A busway A | A | R010 | 400 | 3
R010 tap B | busway | 132 kW | Row A busway B | B | R010 | 400 | 3
R011 tap A | busway | 132 kW | Row A busway A | A | R011 | 400 | 3
R011 tap B | busway | 132 kW | Row A busway B | B | R011 | 400 | 3
R012 tap A | busway | 132 kW | Row A busway A | A | R012 | 400 | 3
R012 tap B | busway | 132 kW | Row A busway B | B | R012 | 400 | 3
R013 tap A | busway | 15 kW | Row A busway A | A | R013
R013 tap B | busway | 15 kW | Row A busway B | B | R013
Row B busway A | busway | 1656 kW | UPS bank A | A
Row B busway B | busway | 1656 kW | UPS bank B | B
R014 tap A | busway | 132 kW | Row B busway A | A | R014 | 400 | 3
R014 tap B | busway | 132 kW | Row B busway B | B | R014 | 400 | 3
R015 tap A | busway | 132 kW | Row B busway A | A | R015 | 400 | 3
R015 tap B | busway | 132 kW | Row B busway B | B | R015 | 400 | 3
R016 tap A | busway | 132 kW | Row B busway A | A | R016 | 400 | 3
R016 tap B | busway | 132 kW | Row B busway B | B | R016 | 400 | 3
R017 tap A | busway | 132 kW | Row B busway A | A | R017 | 400 | 3
R017 tap B | busway | 132 kW | Row B busway B | B | R017 | 400 | 3
R018 tap A | busway | 132 kW | Row B busway A | A | R018 | 400 | 3
R018 tap B | busway | 132 kW | Row B busway B | B | R018 | 400 | 3
R019 tap A | busway | 132 kW | Row B busway A | A | R019 | 400 | 3
R019 tap B | busway | 132 kW | Row B busway B | B | R019 | 400 | 3
R020 tap A | busway | 132 kW | Row B busway A | A | R020 | 400 | 3
R020 tap B | busway | 132 kW | Row B busway B | B | R020 | 400 | 3
R021 tap A | busway | 132 kW | Row B busway A | A | R021 | 400 | 3
R021 tap B | busway | 132 kW | Row B busway B | B | R021 | 400 | 3
R022 tap A | busway | 132 kW | Row B busway A | A | R022 | 400 | 3
R022 tap B | busway | 132 kW | Row B busway B | B | R022 | 400 | 3
R023 tap A | busway | 132 kW | Row B busway A | A | R023 | 400 | 3
R023 tap B | busway | 132 kW | Row B busway B | B | R023 | 400 | 3
R024 tap A | busway | 132 kW | Row B busway A | A | R024 | 400 | 3
R024 tap B | busway | 132 kW | Row B busway B | B | R024 | 400 | 3
R025 tap A | busway | 132 kW | Row B busway A | A | R025 | 400 | 3
R025 tap B | busway | 132 kW | Row B busway B | B | R025 | 400 | 3
R026 tap A | busway | 15 kW | Row B busway A | A | R026
R026 tap B | busway | 15 kW | Row B busway B | B | R026
Row C busway A | busway | 1656 kW | UPS bank A | A
Row C busway B | busway | 1656 kW | UPS bank B | B
R027 tap A | busway | 132 kW | Row C busway A | A | R027 | 400 | 3
R027 tap B | busway | 132 kW | Row C busway B | B | R027 | 400 | 3
R028 tap A | busway | 132 kW | Row C busway A | A | R028 | 400 | 3
R028 tap B | busway | 132 kW | Row C busway B | B | R028 | 400 | 3
R029 tap A | busway | 132 kW | Row C busway A | A | R029 | 400 | 3
R029 tap B | busway | 132 kW | Row C busway B | B | R029 | 400 | 3
R030 tap A | busway | 132 kW | Row C busway A | A | R030 | 400 | 3
R030 tap B | busway | 132 kW | Row C busway B | B | R030 | 400 | 3
R031 tap A | busway | 132 kW | Row C busway A | A | R031 | 400 | 3
R031 tap B | busway | 132 kW | Row C busway B | B | R031 | 400 | 3
R032 tap A | busway | 132 kW | Row C busway A | A | R032 | 400 | 3
R032 tap B | busway | 132 kW | Row C busway B | B | R032 | 400 | 3
R033 tap A | busway | 132 kW | Row C busway A | A | R033 | 400 | 3
R033 tap B | busway | 132 kW | Row C busway B | B | R033 | 400 | 3
R034 tap A | busway | 132 kW | Row C busway A | A | R034 | 400 | 3
R034 tap B | busway | 132 kW | Row C busway B | B | R034 | 400 | 3
R035 tap A | busway | 132 kW | Row C busway A | A | R035 | 400 | 3
R035 tap B | busway | 132 kW | Row C busway B | B | R035 | 400 | 3
R036 tap A | busway | 132 kW | Row C busway A | A | R036 | 400 | 3
R036 tap B | busway | 132 kW | Row C busway B | B | R036 | 400 | 3
R037 tap A | busway | 132 kW | Row C busway A | A | R037 | 400 | 3
R037 tap B | busway | 132 kW | Row C busway B | B | R037 | 400 | 3
R038 tap A | busway | 132 kW | Row C busway A | A | R038 | 400 | 3
R038 tap B | busway | 132 kW | Row C busway B | B | R038 | 400 | 3
R039 tap A | busway | 15 kW | Row C busway A | A | R039
R039 tap B | busway | 15 kW | Row C busway B | B | R039
Row D busway A | busway | 1656 kW | UPS bank A | A
Row D busway B | busway | 1656 kW | UPS bank B | B
R040 tap A | busway | 132 kW | Row D busway A | A | R040 | 400 | 3
R040 tap B | busway | 132 kW | Row D busway B | B | R040 | 400 | 3
R041 tap A | busway | 132 kW | Row D busway A | A | R041 | 400 | 3
R041 tap B | busway | 132 kW | Row D busway B | B | R041 | 400 | 3
R042 tap A | busway | 132 kW | Row D busway A | A | R042 | 400 | 3
R042 tap B | busway | 132 kW | Row D busway B | B | R042 | 400 | 3
R043 tap A | busway | 132 kW | Row D busway A | A | R043 | 400 | 3
R043 tap B | busway | 132 kW | Row D busway B | B | R043 | 400 | 3
R044 tap A | busway | 132 kW | Row D busway A | A | R044 | 400 | 3
R044 tap B | busway | 132 kW | Row D busway B | B | R044 | 400 | 3
R045 tap A | busway | 132 kW | Row D busway A | A | R045 | 400 | 3
R045 tap B | busway | 132 kW | Row D busway B | B | R045 | 400 | 3
R046 tap A | busway | 132 kW | Row D busway A | A | R046 | 400 | 3
R046 tap B | busway | 132 kW | Row D busway B | B | R046 | 400 | 3
R047 tap A | busway | 132 kW | Row D busway A | A | R047 | 400 | 3
R047 tap B | busway | 132 kW | Row D busway B | B | R047 | 400 | 3
R048 tap A | busway | 132 kW | Row D busway A | A | R048 | 400 | 3
R048 tap B | busway | 132 kW | Row D busway B | B | R048 | 400 | 3
R049 tap A | busway | 132 kW | Row D busway A | A | R049 | 400 | 3
R049 tap B | busway | 132 kW | Row D busway B | B | R049 | 400 | 3
R050 tap A | busway | 132 kW | Row D busway A | A | R050 | 400 | 3
R050 tap B | busway | 132 kW | Row D busway B | B | R050 | 400 | 3
R051 tap A | busway | 132 kW | Row D busway A | A | R051 | 400 | 3
R051 tap B | busway | 132 kW | Row D busway B | B | R051 | 400 | 3
R052 tap A | busway | 15 kW | Row D busway A | A | R052
R052 tap B | busway | 15 kW | Row D busway B | B | R052
Row E busway A | busway | 1656 kW | UPS bank A | A
Row E busway B | busway | 1656 kW | UPS bank B | B
R053 tap A | busway | 132 kW | Row E busway A | A | R053 | 400 | 3
R053 tap B | busway | 132 kW | Row E busway B | B | R053 | 400 | 3
R054 tap A | busway | 132 kW | Row E busway A | A | R054 | 400 | 3
R054 tap B | busway | 132 kW | Row E busway B | B | R054 | 400 | 3
R055 tap A | busway | 132 kW | Row E busway A | A | R055 | 400 | 3
R055 tap B | busway | 132 kW | Row E busway B | B | R055 | 400 | 3
R056 tap A | busway | 132 kW | Row E busway A | A | R056 | 400 | 3
R056 tap B | busway | 132 kW | Row E busway B | B | R056 | 400 | 3
R057 tap A | busway | 132 kW | Row E busway A | A | R057 | 400 | 3
R057 tap B | busway | 132 kW | Row E busway B | B | R057 | 400 | 3
R058 tap A | busway | 132 kW | Row E busway A | A | R058 | 400 | 3
R058 tap B | busway | 132 kW | Row E busway B | B | R058 | 400 | 3
R059 tap A | busway | 132 kW | Row E busway A | A | R059 | 400 | 3
R059 tap B | busway | 132 kW | Row E busway B | B | R059 | 400 | 3
R060 tap A | busway | 132 kW | Row E busway A | A | R060 | 400 | 3
R060 tap B | busway | 132 kW | Row E busway B | B | R060 | 400 | 3
R061 tap A | busway | 132 kW | Row E busway A | A | R061 | 400 | 3
R061 tap B | busway | 132 kW | Row E busway B | B | R061 | 400 | 3
R062 tap A | busway | 132 kW | Row E busway A | A | R062 | 400 | 3
R062 tap B | busway | 132 kW | Row E busway B | B | R062 | 400 | 3
R063 tap A | busway | 132 kW | Row E busway A | A | R063 | 400 | 3
R063 tap B | busway | 132 kW | Row E busway B | B | R063 | 400 | 3
R064 tap A | busway | 132 kW | Row E busway A | A | R064 | 400 | 3
R064 tap B | busway | 132 kW | Row E busway B | B | R064 | 400 | 3
R065 tap A | busway | 15 kW | Row E busway A | A | R065
R065 tap B | busway | 15 kW | Row E busway B | B | R065
Row F busway A | busway | 1656 kW | UPS bank A | A
Row F busway B | busway | 1656 kW | UPS bank B | B
R066 tap A | busway | 132 kW | Row F busway A | A | R066 | 400 | 3
R066 tap B | busway | 132 kW | Row F busway B | B | R066 | 400 | 3
R067 tap A | busway | 132 kW | Row F busway A | A | R067 | 400 | 3
R067 tap B | busway | 132 kW | Row F busway B | B | R067 | 400 | 3
R068 tap A | busway | 132 kW | Row F busway A | A | R068 | 400 | 3
R068 tap B | busway | 132 kW | Row F busway B | B | R068 | 400 | 3
R069 tap A | busway | 132 kW | Row F busway A | A | R069 | 400 | 3
R069 tap B | busway | 132 kW | Row F busway B | B | R069 | 400 | 3
R070 tap A | busway | 132 kW | Row F busway A | A | R070 | 400 | 3
R070 tap B | busway | 132 kW | Row F busway B | B | R070 | 400 | 3
R071 tap A | busway | 132 kW | Row F busway A | A | R071 | 400 | 3
R071 tap B | busway | 132 kW | Row F busway B | B | R071 | 400 | 3
R072 tap A | busway | 132 kW | Row F busway A | A | R072 | 400 | 3
R072 tap B | busway | 132 kW | Row F busway B | B | R072 | 400 | 3
R073 tap A | busway | 132 kW | Row F busway A | A | R073 | 400 | 3
R073 tap B | busway | 132 kW | Row F busway B | B | R073 | 400 | 3
R074 tap A | busway | 132 kW | Row F busway A | A | R074 | 400 | 3
R074 tap B | busway | 132 kW | Row F busway B | B | R074 | 400 | 3
R075 tap A | busway | 132 kW | Row F busway A | A | R075 | 400 | 3
R075 tap B | busway | 132 kW | Row F busway B | B | R075 | 400 | 3
R076 tap A | busway | 132 kW | Row F busway A | A | R076 | 400 | 3
R076 tap B | busway | 132 kW | Row F busway B | B | R076 | 400 | 3
R077 tap A | busway | 132 kW | Row F busway A | A | R077 | 400 | 3
R077 tap B | busway | 132 kW | Row F busway B | B | R077 | 400 | 3
R078 tap A | busway | 15 kW | Row F busway A | A | R078
R078 tap B | busway | 15 kW | Row F busway B | B | R078
R079 tap A | busway | 40 kW | UPS bank A | A | R079
R079 tap B | busway | 40 kW | UPS bank B | B | R079

## Networks
vlan | name | purpose | subnet

## Links
site_a | site_b | type | bandwidth_gbps | latency_ms | utilization_pct | protected | carrier

## Cooling
name | type | capacity_kw | serves | model
Rear door R001 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R002 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R003 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R004 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R005 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R006 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R007 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R008 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R009 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R010 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R011 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R012 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R013 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R014 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R015 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R016 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R017 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R018 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R019 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R020 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R021 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R022 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R023 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R024 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R025 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R026 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R027 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R028 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R029 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R030 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R031 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R032 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R033 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R034 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R035 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R036 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R037 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R038 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R039 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R040 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R041 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R042 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R043 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R044 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R045 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R046 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R047 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R048 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R049 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R050 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R051 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R052 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R053 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R054 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R055 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R056 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R057 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R058 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R059 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R060 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R061 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R062 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R063 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R064 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R065 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R066 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R067 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R068 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R069 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R070 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R071 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R072 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R073 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R074 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R075 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R076 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R077 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R078 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor
Rear door R079 | rear door | 75 |  | rear_door_hx/motivair/chilleddoor

## CustomDevices
name | category | brand | model | height_u | width_in | depth_mm | weight_kg | psu_count | psu_w | idle_w | typical_w | max_w | airflow | inlet_max_c | ports | extra_json